INFORMATION RELATIVE TO

THE DRAFT TITLE V OPERATING PERMIT

August x, 2025

GENERAL FACILITY INFORMATION

Facility Name:  TVA Magnolia Combined Cycle

Facility Address: 352 Highway 4 West, Ashland, MS 38603

County: Benton

SIC Code(s): 4911

NAICS Code(s): 22111

APPLICATION SUMMARY

| Permit No.: 0200-00019 Permit Action: Renewal Permit Folder: PER20240001 Application Receipt Date: 11/25/2024 Application Deemed Complete: 01/13/2025 CBI Submitted? No | NSPS (Part 60): Da, Dc, GG, IIII NESHAP (Part 61): N/A NESHAP (Part 63): ZZZZ 112(r) / RMP: N/A Other: Acid Rain Regulations, CSAPR |
| --- | --- |

FACILITY DESCRIPTION

Tennessee Valley Authority operates the existing TVA Magnolia Combined Cycle (MCC) electric generating plant in Benton County, MS, where the facility has nominal and maximum generation capacities of 930 megawatts (MW) and 968 MW, respectively. MCC operates, as needed, to provide intermediate or baseload power generation and reliable support for the electric transmission system. The following table contains a detailed list of the significant emission points contained in the proposed permit.

| Emission Point | Reference Number | Description |
| --- | --- | --- |
| AA-001 | MCC01 | 2,336 MMBtu/hr (170 MW) natural gas-fired Combined Cycle Combustion Turbine with a Heat Recovery Steam Generator (HRSG) equipped with a 610.5 MMBtu/hr duct burner. The combustion turbine is equipped with dry low-NOx burners and a Selective Catalytic Reduction (SCR) system which uses aqueous ammonia as a reducing agent to control NOx emissions from the exhaust of the combined cycle system. (1,726.1 MMBtu/hr for the combustion turbine and 610.5 MMBtu/hr for the duct burner) |
| AA-002 | MCC02 | 2,336 MMBtu/hr (170 MW) natural gas-fired Combined Cycle Combustion Turbine with a HRSG equipped with a 610.5 MMBtu/hr duct burner. The combustion turbine is equipped with dry low-NOx burners and a SCR system which uses aqueous ammonia as a reducing agent to control NOx emissions from the exhaust of the combined cycle system. (1,726.1 MMBtu/hr for the combustion turbine and 610.5 MMBtu/hr for the duct burner) |
| AA-003 | MCC03 | 2,336 MMBtu/hr (170 MW) natural gas-fired Combined Cycle Combustion Turbine with a HRSG equipped with a 610.5 MMBtu/hr duct burner. The combustion turbine is equipped with dry low-NOx burners and a SCR system which uses aqueous ammonia as a reducing agent to control NOx emissions from the exhaust of the combined cycle system. (1,726.1 MMBtu/hr for the combustion turbine and 610.5 MMBtu/hr for the duct burner) |
| AA-004 | AB01 | 69.8 MMBtu/hr natural gas-fired Auxiliary Boiler |
| AA-009 | ---- | 1.89 MMBtu/hr (270 hp) diesel-fired Emergency Fire Pump Engine (Manufactured: 2002) |
| AA-010 | AC01 | 0.84 MMBtu/hr (115 hp) diesel-fired engine for the Air Compressor (Manufactured: 2014) |
| AA-011 | --- | 22.6 MMBtu/hr (3,352 hp/2,500 kW) diesel-fired Emergency Generator Engine (Manufactured 2025) |

TITLE V SOURCE APPLICABILITY

The facility’s potential-to-emit (PTE) exceeds the Title V major source threshold of 100 tons per year (tpy) for each of the following criteria air pollutants: Nitrogen Oxides (NOx), Carbon Monoxide (CO), Sulfur Dioxide (SO2), Particulate Matter less than 10 microns (PM10), Particulate Matter less than 2.5 microns (PM2.5), and/or Volatile Organic Compounds (VOC). The facility’s potential-to-emit hazardous air pollutants (HAPs) does not exceed the major source threshold of 25 tpy of total HAPs and 10 tpy for any individual HAP. The facility is considered an area source of HAP.

Facility-Wide Potential-to-Emit Summary1

| Pollutant | PTE Emissions (tons/yr) |
| --- | --- |
| Particulate Matter (TSP) | 352 |
| PM10 | 352 |
| PM2.5 | 352 |
| Sulfur Dioxide (SO2) | 15.7 |
| Nitrogen Oxides (NOx) | 556 |
| Carbon Monoxide (CO) | 1,812 |
| Volatile Organic Compounds (VOC) | 229 |
| Total Reduced Sulfur (TRS) | 0.00 |
| Lead | 0.01 |
| CFC/HCFC | 0.00 |
| Total HAP | 16.6 |

1 The PTE emissions reflect any emission limits or enforceable restrictions included in the proposed permit.

PREVENTION OF SIGNIFICANT DETERIORATION (PSD) APPLICABILITY

The facility is one of the 28 categorical facilities listed in 40 CFR 52.21(b)(1)(i)(a); therefore, the PSD threshold for a major source is 100 tpy. The facility has the potential to emit more than 100 tons per year of PM/PM10/PM2.5, NOx, CO, and VOC; therefore, the facility is considered a major stationary source. This permitting action will not change the current PSD status of the facility

FACILITY MODIFICATIONS AND/OR PERMIT CHANGES

There are no significant permit changes proposed as part of this permitting action. Minor changes have been proposed in the permit. The most notable revisions include:

- Removed Emission Points AA-005, AA-006, and AA-007 since they are considered Insignificant Activities.

- The previous permit had a daily fuel usage monitoring requirement from 40 CFR 60, Subpart Dc. Since the facility only uses natural gas, the monitoring requirement has been revised to allow monthly fuel usage records as is noted in Subpart Dc.

- Streamlined language in the permit to address federal requirements (i.e., added Section 3.D Work Practice Standards for Emission Point AA-009).

- Added specific monitoring requirements for 40 CFR 60 Da.

- Added a new diesel-fired emergency engine per a 502(b)(10) modification request submitted in January 2026.

COMPLIANCE ASSURANCE MONITORING (CAM) APPLICABILITY

40 CFR Part 64 specifies the requirements for CAM.  The general applicability of this rule can be found in 40 CFR 64.2 and requires a Title V source to comply with the CAM requirements if all three of the following criteria are met for a pollutant-specific emission unit (PSEU):

- The unit is subject to an emission limitation or standard for a regulated air pollutant other than exemptions under 40 CFR 64.2(b)(1);

- The unit uses a control device to comply with the standard; and

- The unit has pre-control emissions exceeding Title V major source threshold.

Emission Points AA-001, AA-002, and AA-003 are equipped with control devices for NOx emissions (i.e., SCR and low NOx burners) such that they are able to meet the applicable BACT and NSPS emission limits. While the uncontrolled NOx emissions exceed the applicable major source threshold of 100 tpy, the emission points are not subject to the CAM provisions since they meet the exemption requirement in 40 CFR 64.2(b)(1)(vi) for the continuous compliance determination method through the installation of a continuous emissions monitoring system (CEMS). The emission points are also potentially subject to the CAM provisions for PM/PM10, VOC, and CO; however, there are no controls for these pollutants. As such, the provisions of CAM are not applicable to these pollutants.

NATIONAL EMISSION STANDARDS FOR HAZARDOUS AIR POLLUTANTS (NESHAP) APPLICABILITY

- NESHAP for Stationary Combustion Turbines, 40 CFR 63, Subpart YYYY - The provisions of Subpart YYYY are applicable to stationary combustion turbines located at major sources of HAP emissions. The facility is not a major source of HAP emissions; therefore, the facility is not subject to the requirements of Subpart YYYY.

- NESHAP for Stationary Reciprocating Internal Combustion Engines, 40 CFR 63, Subpart ZZZZ - The provisions of Subpart ZZZZ are applicable to stationary reciprocating internal combustion engines located at major and area sources of HAP emissions. The facility is considered an area source of HAP emissions. Emission Point AA-009 commenced construction prior to June 12, 2006, and is considered an existing stationary RICE subject to the requirements of Subpart ZZZZ.

Emission Points AA-010 and AA-011 were constructed after June 12, 2006, and are considered new stationary RICE. As such, the facility will comply with Subpart ZZZZ by meeting the applicable requirements of 40 CFR 60, Subpart IIII.

- NESHAP for Major Sources: Industrial, Commercial, and Institutional Boilers and Process Heaters, 40 CFR 63, Subpart DDDDD - The provisions of Subpart DDDDD are applicable to industrial, commercial, and institutional boilers and process heaters located at major sources of HAPs. The facility is not a major source of HAP emissions; therefore, the facility is not subject to the requirements of Subpart DDDDD.

- NESHAP for Industrial, Commercial, and Institutional Boilers Area Sources, 40 CFR 63, Subpart JJJJJJ - The provisions of Subpart JJJJJJ are applicable to industrial, commercial, and institutional boilers located at area sources of HAP emissions. The facility is considered an area source of HAP emissions. Each combustion turbine is equipped with a HRSG that provides steam to the steam turbine and generator, and Emission Point AA-004 is a natural gas-fired industrial boiler. The HRSGs and the auxiliary boiler are natural gas-fired units; therefore, they are not subject to Subpart JJJJJJ per the exemption in 40 CFR 63.11195(e)

- NESHAP for Coal and Oil-Fired Electric Utility Steam Generating Units, 40 CFR 63, Subpart UUUUU - The provisions of Subpart UUUUU are applicable to coal or oil-fired electric utility steam generating units (EGU). The combustion turbines at the facility are considered EGUs; however, they meet the definition of a natural gas-fired EGU in 40 CFR 63.10042. Per 40 CFR 63.9983(b), these combustion turbines are not subject to the requirements of Subpart UUUUU.

NEW SOURCE PERFORMANCE STANDARDS (NSPS) APPLICABILITY

- Standards of Performance for Electric Utility Steam Generating Units, 40 CFR 60, Subpart Da – The provisions of Subpart Da are applicable to electric utility steam generating units (i.e., combined cycle gas turbines equipped with a HRSG duct burner) capable of combusting more than 250 MMBtu/hr heat input. The HRSG duct burners at the facility have a rated heat input in excess of 250 MMBtu/hr; therefore, the duct burners are subject to the applicable requirements of Subpart Da. Since the units are fired with natural gas, the duct burners meet the exemptions in 40 CFR 60.42Da and are not required to meet the PM or Opacity limits. The facility complies with the SO2 limit by keeping fuel purchase records that detail the sulfur content of the fuel being fired. The information collected using the NOx CEMS required under Part 75 is used to demonstrate compliance with the Subpart Da limit on NOx. Emission Point AA-004 is an electric utility steam generating unit but has a maximum heat input of 69.8 MMBtu/hr; therefore, it is not subject to the requirements of Subpart Da.

- Standards of Performance for Industrial-Commercial-Institutional Steam Generating Units, 40 CFR 60, Subpart Db – The provisions of Subpart Db are applicable to Industrial-Commercial-Institutional Steam Generating Units with a heat input capacity from fuels combusted in the steam generating unit of greater than 100 MMBtu/hr. Emission Points AA-001, AA-002, and AA-003 were constructed after the applicability date and have a heat input capacity greater than 100 MMBtu/hr; however, per 40 CFR 60.40b(e) steam generating units meeting the applicability requirements under Subpart Da are not subject to the Subpart Db requirements. Emission Point AA-004 has a maximum heat input of 69.8 MMBtu/hr; therefore, it is not subject to the requirements of Subpart Db.

- Standards of Performance for Small Industrial-Commercial-Institutional Steam Generating Units, 40 CFR 60, Subpart Dc – The provisions of Subpart Dc are applicable to steam generating units that were constructed after June 9, 1989, and have a maximum heat input capacity of 100 MMBtu/hr or less but greater than or equal to 10 MMBtu/hr. The duct burners associated with Emission Points AA-001, AA-002, and AA-003 each have a maximum heat input of 610.5 MMBtu/hr; therefore, they are not subject to the requirements of Subpart Dc. Emission Point AA-004 has a maximum heat input capacity of 69.8 MMBtu/hr; therefore, it is subject to the requirements of Subpart Dc. However, even though the boiler is subject to the requirements of Subpart Dc, the unit is fired with natural gas only. As such, the only applicable requirement for the unit is to monitor and record the monthly fuel usage.

- Standards of Performance for Stationary Gas Turbines, 40 CFR 60, Subpart GG - The provisions of Subpart GG are applicable to stationary gas turbines with a heat input at peak load in excess of 10 MMBtu/hr that are constructed after October 3, 1977. The combustion turbines at the facility are subject to the requirements of Subpart GG since they were constructed after this date and have a rated heat input in excess of 10 MMBtu/hr. The units are subject to the NOx and SO2 requirements under Subpart GG. The facility uses the CEMS required under Part 75 to demonstrate compliance with the NOx limit and fuel purchase records to demonstrate compliance with the fuel sulfur content requirement.

- Standards of Performance for Stationary Compression Ignition Internal Combustion Engines, 40 CFR 60, Subpart IIII - The provisions of Subpart IIII are applicable to stationary compression ignition (CI) internal combustion engines (ICE) that commenced construction after July 11, 2005, and where the engine was manufactured after April 1, 2006. Emission Point AA-009  is not subject to Subpart IIII because the engine was constructed prior to the applicability date and has not been modified or reconstructed.

Emission Points AA-010 and AA-011 are subject to the Subpart IIII requirements since the engines were constructed and manufactured after the applicability dates. The applicable provisions of Subpart IIII are included in the proposed permit.

- Standards of Performance for Stationary Combustion Turbines, 40 CFR 60, Subpart KKKK The provisions of Subpart KKKK are applicable to stationary combustion turbines with a heat input at peak load equal to or greater than 10 MMBtu/hr that commenced construction, modification, or reconstruction after February 18, 2005. The combustion turbines associated with Emission Points AA-001 through AA-003 were constructed prior to the applicability date, and they have not been modified or reconstructed, so they are not subject to the provisions of Subpart KKKK.

- Standards of Performance for Greenhouse Gas Emissions for Electric Generating Units, 40 CFR 60, Subpart TTTT - The provisions of Subpart TTTT are applicable to stationary combustion turbines that commenced construction after January 8, 2014, or commenced modification or reconstruction after June 18, 2014. The stationary combustion turbines associated with Emission Points AA-001 through AA-003 were constructed prior to this date and have not been modified or reconstructed, so they are not subject to the provisions of Subpart TTTT.

SPECIFIC APPLICABLE REQUIREMENTS

| Emission Point No. | Pollutant | Draft Permit Emission Limits | Monitoring Requirements |
| --- | --- | --- | --- |
| AA-001 AA-002 AA-003 | SO2 | Emissions shall not exceed 0.80 lb/MMBtu and 10 percent of the potential combustion concentration or 0.20 lbs/MMBtu and 100 percent of the combustion concentration | Fuel certification records |
|  | NOx | ≤ 1.6 lbs/MWh gross energy output | CEMS |
|  | Fuel Sulfur Content | ≤ 0.8% by weight | Fuel certification records |
|  | Fuel Requirement | Natural gas only | Fuel records |
|  | Operating Requirement | Operate the SCR system as soon as and as long as the unit operating conditions are amenable to its effective use. | Keep operating records |
| AA-001 AA-002 AA-003 All Methods of Operation | Smoke | Opacity ≤ 10% | EPA Method 22 or Method 9 VEE |
|  | PM/PM10 (filterable) | ≤ 351 tpy based on a 12-month rolling average | Calculate and maintain records of emissions |
|  | SO2 | ≤ 15.5 tpy based on a 12-month rolling average |  |
|  | NOx | ≤ 530 tpy based on a 12-month rolling average | CEMS Calculate and maintain records of emissions |
|  | CO | ≤ 1,792 tpy based on a 12-month rolling average |  |
|  | NMVOC | ≤ 227 tpy based on a 12-month rolling average | 5-year Performance Test Calculate and maintain records of emissions |
|  | Operating Requirement | Definition of startup, shutdown, and tuning | Monitor and maintain records of operations during startup, shutdown, or tuning |
| AA-001 AA-002 AA-003 With Ducts Firing | PM/PM10 (filterable) | ≤ 27.3 lbs/hr | Calculate and maintain records of emissions |
|  | SO2 | ≤ 7.4 lbs/hr |  |
|  | NOx | ≤ 3.5 ppm @ 15% oxygen on a dry basis, not to exceed 34.3 lbs/hr, both limits are based on a 3-hr rolling average | CEMS |
| AA-001 AA-002 AA-003 With Ducts Firing | CO | ≤ 20 ppm @ 15% oxygen on a dry basis, not to exceed 97.9 lbs/hr, both limits are based on a 3-hr rolling average | CEMS |
|  | NMVOC | ≤ 16.4 lbs/hr | Performance testing Calculate and maintain records of emissions |
|  | GHG | ≤ 1,000 lbs CO2 per MW-hour (gross) | Calculate and maintain records of emissions |
| AA-001 AA-002 AA-003 Without Ducts Firing | PM/PM10 (filterable) | ≤ 20.5 lbs/hr | Calculate and maintain records of emissions |
|  | SO2 | ≤ 5.9 lbs/hr |  |
|  | NOx | ≤ 3.5 ppm at 15% oxygen on a dry basis, not to exceed 27.9 lbs/hr, both limits are based on a 3-hr rolling average during Combined Cycle operations. | CEMS |
|  | CO | ≤ 7.6 ppm @ 15% oxygen on a dry basis, not to exceed 33.5 lbs/hr, both limits are based on a 3-hr rolling average |  |
|  | NMVOC | ≤ 3.2 lbs/hr | 5-year Performance Test Calculate and maintain records of emissions |
|  | GHG | ≤ 1,000 lbs CO2 per MW-hour (gross) | Calculate and maintain records of emissions |
| AA-001 AA-002 AA-003 AA-004 | PM (filterable) | Emissions shall not exceed E = 0.8808*I-0.1667 | The margin of compliance is significant and warrants no additional monitoring |
|  | SO2 | 4.8 lbs/MMBtu |  |
| AA-004 AA-001 AA-002 AA-003 With Ducts Firing | SO2 | Emissions shall not exceed ≤ 4.8 lbs/MMBtu | The margin of compliance is significant and warrants no additional monitoring |
| AA-004 | Hours of Operation | ≤ 4,500 hrs/yr on a rolling 12-month total | Keep operating records |
|  | NOx | ≤ 6.2 lbs/hr and 13.95 TPY | Performance testing Calculate and maintain records of emissions |
| AA-004 | Smoke | Opacity ≤ 10% | EPA Method 22 or Method 9 VEE |
| AA-009 | HAP | Operating requirements | Keep records documenting hours of operation and reason for operation |
| AA-009 AA-010 | PM (filterable) | Emissions shall not exceed ≤ 0.6 MMBtu/hr | The margin of compliance is significant and warrants no additional monitoring |
| AA-010 | PM (filterable) | ≤ 0.02 gram/kW-hr | Backpressure Monitor Recordkeeping Purchase, install, and maintain a certified engine |
|  | NOx | ≤ 0.40 gram/kW-hr | Purchase, install, and maintain a certified engine |
|  | NMHC | ≤ 0.19 gram/kW-hr |  |
|  | CO | ≤ 5.0 gram/kW-hr |  |
| AA-011 | PM (filterable) | ≤ 0.20 gram/kW-hr | Purchase, install, and maintain a certified engine |
|  | NOx + NMHC | ≤ 6.40 gram/kW-hr |  |
|  | CO | ≤ 3.50 gram/kW-hr |  |
|  | PM (filterable) NOx + NMHC CO | Operating requirements | Install non-resettable hour meter and record hours of operation on a calendar year basis |
|  | PM (filterable) | Emissions shall not exceed E = 0.8808*I-0.1667 | The margin of compliance is expected to be significant and warrants no additional monitoring |
| AA-010 AA-011 | SO2 (Diesel fuel requirements) | Maximum sulfur content of 15 ppm AND minimum cetane index of 40 OR maximum aromatic content of 35 volume percent | A large margin of compliance is expected so no additional monitoring is required |
|  | Opacity | ≤ 20 percent during the acceleration mode ≤ 15 percent during the lugging mode ≤ 50 percent during the peaks in the acceleration or lugging mode |  |

OTHER REQUIREMENTS:

Emission Points AA-001 through AA-003 are subject to the provisions of the Acid Rain Program found in 40 CFR 72-78. The permit addresses the provisions of the Acid Rain program in Section 8 of the proposed TVOP and the proposed Phase II Acid Rain Permit is in Appendix C of the proposed TVOP.

Emission Points AA-001 through AA-003 are subject to the applicable requirements of 40 CFR 97, Subpart EEEEE, Cross-State Air Pollution Rule (CSAPR) NOx Ozone Season Group 2 Trading Program. The provisions of Subpart EEEEE are included in Section 9 of the proposed TVOP.