# PERMIT REVIEW SUMMARY

Permit Writer:	Jeffrey Bland	Date: June 23, 2026

Company Name:	Tennessee Gas Pipeline Company LLC, Bellewood Compressor Station Number 602

Facility Location:	Bellewood Road, Isola, MS 38754

Source Number: 1180-00030 County:	Humphreys FACILITY DESCRIPTION

Tennessee Gas Pipeline Company LLC (TGP) proposes to construct the new Bellewood Compressor Station No. 602 (CS 602) near Isola, Mississippi. CS 602 is one of three compressor stations that are part of the proposed TGP Mississippi Crossing Project (MSX Project). The MSX Project consists of approximately 208 miles of new pipeline and associated facilities in the states of Mississippi and Alabama, designed to transport natural gas from TGP's 100 line near Greenville, Mississippi, to interconnections with other pipeline companies in Attala County and Humphreys County, Mississippi and Choctaw County, Alabama.CS 602 will receive low-pressure inlet natural gas and compress the gas to increase the pressure in the pipeline and maintain the downstream flow. The proposed compressor station will be built with bi-directional piping to allow for flow in either direction.

At the compressor station, waste oil, water, and condensate liquids (from routine maintenance operations) may be loaded, as necessary, onto trucks for disposal. There will be two (2) liquid storage tanks for purposes of condensate storage and two (2) emergency backup generator engines. Two (2) catalytic heaters will be used to heat the fuel supply line for the turbines. Gas will be compressed using three (3) compressor turbines. There will also be natural gas blowdowns and fugitive emissions from piping and equipment components. The following table includes the emission points at the facility.

| Emission Point | Description |
| --- | --- |
| AA-001 | 31,900 horsepower (hp) (23.1 Megawatt (MW)) Solar Titan Model No. T250 natural gas-fired simple cycle compressor turbine No. 1 |
| AA-002 | 31,900 HP (23.1 MW) Solar Titan Model No. T250 natural gas-fired simple cycle compressor turbine No. 2 |
| AA-003 | 31,900 HP (23.1 MW) Solar Titan Model No. T250 natural gas-fired simple cycle compressor turbine No. 3 |
| AA-004 | 2,682 HP Caterpillar Model G3520 spark ignition (SI) natural gas-fired emergency backup power generating engine No. 1 |
| AA-005 | 2,682 HP Caterpillar Model G3520 SI natural gas-fired emergency backup power generating engine No. 2 |
| AA-006 | Natural gas-fired catalytic heater No. 1 (less than 10 MMBTUH) |
| AA-007 | Natural gas-fired catalytic heater No. 2 (less than 10 MMBTUH) |
| AA-008 | Fugitive emissions from equipment leaks |
| AA-009 | Natural gas blowdowns |
| AA-010 | 5,000 gallon condensate storage tank (ST-1) |
| AA-011 | 5,000 gallon condensate storage tank (ST-2) |
| AB-001 | Centrifugal compressor driven by Emission Point AA-001 |
| AB-002 | Centrifugal compressor driven by Emission Point AA-002 |
| AB-003 | Centrifugal compressor driven by Emission Point AA-003 |

## PROJECT/PERMIT ACTION DESCRIPTION

CS 602 is classified as a major source with respect to Title V of the Federal Clean Air Act. The facility has the uncontrolled potential to emit greater than 100 tons per year (tpy) of the criteria pollutants Nitrogen Oxides (NOx) and Carbon Monoxide (CO). CS 602 has the uncontrolled potential to emit less than 25 tpy of combined hazardous air pollutants (HAPs), as well as less than 10 tpy of each individual HAP.

## EMISSION SUMMARY

Facility-Wide Potential-to-Emit Summary1

| Pollutant | PTE Emissions (tons/yr) |
| --- | --- |
| Particulate Matter (TSP) | 18.70 |
| PM10 | 18.70 |
| PM2.5 | 18.70 |
| Sulfur Dioxide (SO2) | 9.55 |
| Nitrogen Oxides (NOx) | 101.73 |
| Carbon Monoxide (CO) | 132.61 |
| Volatile Organic Compounds (VOC) | 72.26 |
| Formaldehyde | 2.09 |
| Total HAP | 3,49 |

1 The PTE emissions reflect any emission limits or enforceable restrictions included in the proposed permit.

## APPLICABLE/PROPOSED PERMIT LIMITATION

The compressor turbines (Emission Points AA-001, AA-002, and AA-003) are limited to 0.060 lb SO2 /MMBTU (20 grains S/100scf) and 15 ppm NOx at 15% O2 and 150 ppm NOx at 15% O2 when operating at less than 70% of peak load in order to comply with 40 CFR 60, Subpart KKKKa emission limitations. Stack testing for NOx emissions and fuel tariff sheets for SO2 is required for compliance demonstration purposes.

The emergency backup generator engines (Emission Points AA-004 and AA-005) are limited to

2.0 g/HP-hr NOx emissions, 4.0 g/HP-hr CO emissions, and 1.0 g/HP-hr VOC emissions in order to comply with the 40 CFR 60, Subpart JJJJ emission limitations. The facility will demonstrate compliance by purchasing certified engines or by meeting the requirements of 40 CFR 60.4243(b)(2).

The compressors (Emission Points AB-001, AB-002, and AB-003) are limited to less than or equal to 10 standard cubic feet per minute (scfm) per dry seal. Monitoring, recordkeeping, and reporting requirements from Subpart OOOOb are included in the draft permit. Additionally, fugitive equipment leaks are subject to leak detection and repair requirements of Subpart OOOOb.

There are no process controller affected units since none of the facility’s process controllers will be natural gas driven.

## NSPS APPLICABILITY

40 CFR 60 Subpart KKK

The provisions of 40 CFR 60, Subpart KKK - Standards of Performance for Equipment Leaks of VOC from Onshore Natural Gas Processing Plants (NSPS KKK) apply to affected facilities in onshore natural gas processing plants that commences construction, reconstruction, or modification after January 20, 1984, and on or before August 23, 2011. Since CS 602 is not located at an onshore natural gas processing plant, as defined in 40 CFR 60.631, and will be constructed after the applicability date, the Bellewood Compressor Station is not subject to NSPS KKK.

40 CFR 60 Subpart IIII

The provisions of 40 CFR 60 Subpart IIII - New Source Performance Standards for Compression Ignition Internal Combustion Engines (NSPS IIII) are applicable to stationary compression ignition internal combustion engines that commenced construction, modification, or reconstruction after April 1, 2006. None of the compressor station’s engines are compression ignition internal combustion engines, therefore, none of the compressor station’s engines are subject to any requirements of NSPS IIII.

40 CFR 60 Subpart JJJJ

The provisions of 40 CFR 60 Subpart JJJJ - New Source Performance Standards for Stationary Spark Ignition Internal Combustion Engines (NSPS JJJJ) are applicable to stationary spark ignition internal combustion engines that commenced construction, modification, or reconstruction after June 12, 2006. The proposed emergency generator engines (Emission Points AA-004 and AA-005) are proposed to be manufactured in 2025 or later. Therefore, each engine is subject to emission standards for NOx, CO and VOC. NOx emissions are limited to 2.0 g/bhp-hr or 270 ppmvd @ 15% O2, CO emissions are limited to 4.0 g/bhp-hr or 540 ppmvd @ 15% O2, and VOC emissions are limited to 1.0 g/bhp-hr or 82 ppmvd @ 15% O2. The engines must be operated and maintained such that each engine achieves these emission standards over the entire life of the engine. To demonstrate compliance with the emission standards in NSPS Subpart JJJJ, the facility will purchase certified engines for Emission Points AA-004 and AA-005.

40 CFR 60 Subpart KKKK

The provisions of 40 CFR 60 Subpart KKKK - New Source Performance Standards for Stationary Combustion Turbines (NSPS KKKK) are applicable to stationary combustion turbines with a heat input at peak load equal to or greater than 10.7 gigajoules (10 MMBtu) per hour, based on the higher heating value of the fuel, which commenced construction, modification, or reconstruction after February 18, 2005.  Since each of the facility’s proposed turbines (Emission Points AA-001 through AA-003) will have construction dates after the NSPS KKKKa effective date, the units are subject to the applicable provisions of NSPS KKKKa and not subject to NSPS KKKK.

40 CFR 60 Subpart KKKKa

The provisions of 40 CFR 60 Subpart KKKKa - New Source Performance Standards for Stationary Combustion Turbines that commenced construction, modification, or reconstruction after December 13, 2024 (NSPS KKKKa) establishes emission standards and compliance schedules for the control of emissions from stationary combustion turbines that commenced construction, modification, or reconstruction after December 13, 2024.  Each of the facility’s proposed turbines will have construction dates after the NSPS KKKKa effective date. Therefore, each unit will be subject to the applicable NOx and SO2 emission standards.

TGP is constructing simple cycle turbines, each with a base load greater than 10 MMBtu/hr which will be subject to Subpart KKKKa. CS 602 has elected to use the lowest NOx emission standard that is applicable as determined using Table 1 to subpart KKKKa for combustion turbine type of new, firing natural gas, at a utilization rate > 45 percent, turbine base load heat input of > 50 MMBtu/hr and ≤ 850 MMBtu/hr. The standard is 15 ppm at 15 percent O2.

By meeting the 15 ppm NOx emission standard without using SCR control technology, TGP is allowed to conduct initial performance testing on each turbine to demonstrate initial compliance and demonstrate continuous compliance by conducting annual performance testing.

40 CFR 60 Subpart OOOO

The provisions of 40 CFR 60, Subpart OOOO - Standards of Performance for Crude Oil and Natural Gas Facilities for Which Construction, Modification, or Reconstruction Commenced After August 23, 2011, and on or Before September 18, 2015 (NSPS OOOO) are potentially applicable to owners and operators of onshore affected facilities that commence construction, modification, or reconstruction between August 23, 2011, and September 18, 2015. Since the facility’s construction date is after September 18, 2015, no sources at the compressor station are subject to any requirements of NSPS OOOO.

40 CFR 60 Subpart OOOOa

The provisions of 40 CFR 60, Subpart OOOOa - Standards of Performance for Crude Oil and Natural Gas Facilities for which Construction, Modification or Reconstruction Commenced After September 18, 2015 and On or Before December 6, 2022 (NSPS OOOOa) are potentially applicable to new and modified sources in the oil and gas industry between August 18, 2015, and December 6, 2022. Since the facility’s construction date is after December 6, 2022, no sources at the compressor station are subject to any requirements of NSPS OOOOa.

40 CFR 60 Subpart OOOOb

The provisions of 40 CFR 60, Subpart OOOOb - Standards of Performance for Crude Oil and Natural Gas Facilities for Which Construction, Modification or Reconstruction Commenced After December 6, 2022 (NSPS OOOOb) are potentially applicable to new and modified sources in the oil and gas industry after December 6, 2022.

The compressors (Emission Points AB-001, AB-002, and AB-003) at the facility are subject to Subpart OOOOb and are limited to less than or equal to 10 standard cubic feet per minute (scfm) per dry seal, Monitoring, recordkeeping, and reporting requirements from Subpart OOOOb are included in the draft permit.

The condensate storage tanks (Emission Points AA-010 and AA-011) meet the definition of storage vessel as defined in 40 CFR 60.5430b. The facility is not considered a storage vessel affected facility per 40 CFR 60.5365b(e) since the potential VOC emissions from the storage vessels are less than 6 tpy and the potential methane emissions are less than 20 tpy. The facility will maintain record of the PTE to verify non-applicability of storage vessel affected facility requirements.

The fugitive emissions components are the components (e.g., pumps, valves, and connectors) assembled to support a process unit, which is a unit (e.g., natural gas processing) that can operate independently if supplied with sufficient feed and storage. The fugitive emissions components at TGP will be constructed after the NSPS OOOOb effective date. Therefore, the fugitive emission components (Emission Point AA-008) are subject to the LDAR requirements of NSPS OOOOb.

40 CFR 60 Subpart Kc

The provisions of 40 CFR 60, Subpart Kc - Standards of Performance for Volatile Organic Liquid Storage Vessels (Including Petroleum Liquid Storage Vessels) for Which Construction, Reconstruction, or Modification Commenced After October 4, 2023, are standards applicable to vessels used for storing volatile organic liquids. The facility’s condensate and maintenance liquids storage tanks are each below the 20,000 gallon threshold; therefore, the facility’s maintenance liquids storage tanks are not subject to NSPS Kc.

## MACT APPLICABILITY

NATIONAL EMISSION STANDARDS FOR HAZARDOUS AIR POLLUTANTS (NESHAP) APPLICABILITY

The facility is considered an area source of Hazardous Air Pollutants (HAP) since the facility does not have the potential to emit more than 25 tons per year of total HAP or 10 tpy of any individual HAP.

40 CFR 63 Subpart ZZZZ - National Emissions Standards for Hazardous Air Pollutants for Stationary Reciprocating Internal Combustion Engines

The Reciprocating Internal Combustion Engines (RICE) NESHAP, Subpart ZZZZ, regulates HAP emissions from RICE.

Emission Points AA-004 and AA-005 are considered a new, spark ignition, 4-stroke lean-burn, emergency engine with a site rating greater than 500 HP that are located at an area source of HAP emissions. As such, the engines must also meet the requirements of Subpart ZZZZ by meeting the requirements of 40 CFR 60, subpart JJJJ, for spark ignition engines. No further requirements apply for such engines under 40 CFR 63 Subpart ZZZZ or the General Provisions of Subpart A.

40 CFR 63 Subpart JJJJJJ - National Emission Standards for Hazardous Air Pollutants for Industrial, Commercial, and Institutional Boilers Area Sources

Since CS 602 is an area source of Hazardous Air Pollutant (HAP) emissions, the facility is potentially subject to 40 CFR 63, Subpart JJJJJJ However, since the Compressor Station does not operate any boilers, none of the facility’s combustion sources are subject to Subpart JJJJJJ or to any requirements in Subpart JJJJJJ.

40 CFR 63 Subpart HHH - National Emission Standards for Hazardous Air Pollutants From Oil and Natural Gas Production Facilities

The provisions of Subpart HHH are applicable to natural gas transmission and storage facilities that transport or store natural gas prior to entering the pipeline to a local distribution company or to a final end user and is considered a major source of HAP emissions. The facility is not a major source of HAP; therefore, the facility is not subject to the requirements of Subpart HHH.

## PUBLIC PARTICIPATION

The 30-day public notice period began on July 1, 2026 , when the notice was posted on MDEQ’s website and ends July 31, 2026 .

## RECOMMENDATION

The staff has preliminarily decided to recommend issuance of the permit to the Mississippi Environmental Quality Permit Board as shown in the draft permit. However, the staff recommendation to the Board will be made only after a thorough consideration of all public comments.