# PUBLIC NOTICE PRETREATMENT RATIONALE FOR ISSUANCE

# Canton, City of, Canton Sanitary Landfill

# Madison County

# Canton, MS

# Water II Branch

# MSP092474

# SIC: 4953

# July 13, 2026

# Permit Engineer: Rusty Parrish

# FACILITY INFORMATION

## Nature of Business: Municipal Solid Waste Landfill

## Process Wastewater Description: Process wastewater is generated from landfill leachate.

## Proposed Flowrate: 0.048 MGD

- Applicable Federal Guidelines: 40 CFR Part 403 – General Pretreatment Reguations

# RECEIVING POTW INFORMATION

## POTW Name, AI No., and Permit No.: Canton POTW HCR Site; 13051; MS0042455

## POTW Treatment Type: Biological treatment by means of a lagoon system followed by a hydrograph controlled release storage cell.

- POTW Design Flowrate: 2.6 MGD

- POTW Receiving Stream: Bear Creek thence into the Big Black River

- POTW Receiving Stream 7Q10 (Q7/10): 22 cfs = 11.84 MGD

# PERTINENT FLOWRATE AND LOADING DATA

- POTW 12-month Average Flowrate (QPOTW): 1.494 MGD (January 2024 – December 2024)

- Industrial Facilities Maximum 30-day Average Flow (QIND) in MGD for Contributing pollutants (January 2024 – December 2024)

- Industrial Facilities Permitted/Requested Flow in MGD (QW):

# BACKGROUND/DOMESTIC LOADING CALCULATIONS

Background Loading (BGL), lb/d = 8.34 x BGC(mg/L)(1) x (QPOTW - QINDUSTRIAL(2))(MGD)

1 BGC = Background concentration of domestic sewage.  Calculated from literature values from Appendix V of EPA’s Local Limits Development Guidance (EPA 833-R-04-002A, July 2004) for those pollutants with insufficient data (page 115/128).

QIND = (QW1 + QW2 + …) = Summation of maximum 30-day average flows from existing industrial dischargers (IUs) contributing a Pollutant of Concern (POC) to the POTW.

# ALLOWABLE HEADWORKS LOADING CALCULATIONS

Instream Wastewater Concentration (IWC), % = [QPOTW / (QPOTW + Q7/10)] x 100

- Allowable Water Quality Criteria (AWQC) Headworks Loading Calculations

HLWQC, lb/day = 8.34 x CCRITERIA (mg/L) x (Q7/10 + QPOTW, MGD) / (1 – RPOTW)

CCRITERIA = Water Quality Criteria; obtained from State of Mississippi Water Quality Criteria for Intrastate, Interstate, and Coastal Waters: Freshwater Acute and Chronic Values.

RPOTW = Removal efficiency, in decimal form, from Appendix B in rationale and  Appendix R of EPA’s Local Limits Development Guidance (EPA 833-R-04-002A, July 2004) for those pollutants with insufficient data.

Chronic Analysis, AHLCWQC:

Acute Analysis, AHLAWQC:

# AHL, POTW Inhibition Based (AHLINH)

## AHLINH, lb/day = 8.34 x QPOTW (MGD) x CINH (mg/L)

CINH = Activated Sludge Inhibition Levels, from EPA Guidance Manual on the Development and Implementation of Local Discharge Limitations Under the Pretreatment Program: Table 3-2 Activated Sludge Inhibition Levels.  For the silver parameter, the minimum reported inhibition threshold is utilized.  For all other parameters, 1.0 mg/L is used since this value is near the minimum side of the minimum reported range of inhibition threshold levels.

# AHL, POTW NPDES Permit Limit Based (AHLNPDES)

None.

# MAXIMUM ALLOWABLE HEADWORKS LOADINGS AND LIMITING CASE

MAHLC = smallest chronic AHL = comparison of AHLINH, AHLCWQC, and AHLCNPDES

MAHLA = smallest acute AHL = comparison of AHLINH, AHLAWQC, and AHLANPDES

# LC = smallest of MAHLC and MAHLA

- DEVELOPMENT OF ALLOWABLE CONCENTRATIONS

The remaining industrial wasteload allocation will be used in calculating allowable acute and chronic concentrations using the “Industrial User (IU) Contributory Flow” method as described in EPA’s Local Limits Development Guidance (EPA 833-R-04-002A, July 2004).

PAI, lb/day = (MAHL, lb/day – BGL, lb/day) x (QW, MGD / QT, MGD)

CALLOW, mg/L = (PAI, lb/day) / (8.34 x QW, MGD)

PAI	= 	Permit allocation for indirect discharger

CALLOW	= 	Allowable concentration for indirect discharger

QW		= 	Applicant’s permitted/requested process discharge

QT 		= 	Total industrial contributory flow for pertinent pollutants

MAHL		= 	MAHLC to be used for chronic and MAHLA used for acute

BGL		=	Background/domestic loading

CHRONIC (Average):

ACUTE (Maximum):

- PROPOSED PERMIT LIMITATIONS

BTJ = Best Technical Judgement; CPL = Current Permit Limit

Ammonia (Total as N), Nickel (TR), Zinc (TR), Oil & Grease, BOD5, and TSS shall be monitored twice per month utilizing a grab sample. Flow shall be monitored once per discharge event utilizing a totalizer. pH shall be monitored twice per month utilizing a grab sample.

For the Flow – Effluent parameter, the Daily Maximum shall be reported as the sum of all batch discharges in a single day. A record of each individual discharge shall be maintained in accordance with Condition R-1 of this permit. [11 Miss. Admin. Code Pt. 6, Ch. 1.]

### APPENDIX A

BACKGROUND CONCENTRATION OF DOMESTIC SEWAGE

Calculated from the seven following tables. The literature value from Appendix V of EPA’s Local Limits Development Guidance (EPA 833-R-04-002A, July 2004) was used for Nickel.

DATA FOR NICKEL (Ni) BACKGROUND/ DOMESTIC CONCENTRATION

Average Domestic Concentration for Nickel (Ni) = BGC = 0.0306 mg/L

*These values are the Averages listed on the DMRs. Average values are preferred over Maximum values because they present a more representative model of the facility’s typical effluent.

DATA FOR ZINC (Zn) BACKGROUND/ DOMESTIC CONCENTRATION

Average Domestic Concentration for Zinc (Zi) = 0.8207 mg/L

*These values are the Averages listed on the DMRs. Average values are preferred over Maximum values because they present a more representative model of the facility’s typical effluent.

APPENDIX B

REMOVAL EFFICIENCIES

*Removal Efficiency = [(<inf.> - <eff.>)/<inf.>]*100, where <inf.> is the average influent value and <eff.> is the average effluent value.

Values obtained from POTW bench sheets. Literature Values are highlighted in orange.

Grey-shaded values were excluded because influent ≤ effluent for the same sample date.

Blue values were used in “non-detect” results in which the Method Quantitation Limit (MQL) was then divided by 2 to obtain the blue value.

**Appendix R of EPA’s Local Limits Development Guidance for tertiary treatment was used due to inadequate data from the POTW.

### ADEQUACY OF TREATMENT

Date: November 17, 2025

Permit Writer: Rusty Parrish

Proposed Site: Canton, City of, Canton Sanitary Landfill

Pretreatment Permit No. MSP092474

Madison County

Proposed Flowrate: 0.048 MGD

Proposed Organic Loading: 256 mg/L (Maximum value provided on application)

0.048 MGD * 8.34 * 256 mg/L = 102.48 lbs/day

Canton POTW HCR Site; Permit No. MS0042455; AI #13051

Permitted Flow: 2.6 MGD

12 Month Flow: 1.494 MGD (January 2024 – December 2024)

12 Month BOD5: 5,438.8 lbs/day representative influent value (January 2024 – December 2024)

Design BOD5: 2.6 MGD * 8.34 * 350 mg/L = 7,589 lbs/day

Evaluation of Flow

2.6 MGD permitted flow – 1.494 MGD actual flow = 1.106 MGD

1.106 MGD available vs. 0.048 MGD proposed flowrate

Evaluation of BOD5

7,589 lbs/day Design – 5,438.8 lbs/day (12 Month Average) = 2,150.2 lbs/day

2,150.2 lbs/day available vs. 102.48 lbs/day proposed