# PRETREATMENT RATIONALE FOR RENEWAL

Greenway Environmental Services LLC., 			MSP092246

Green Meadow Sustainable Solutions Landfill		SIC Code 4953

# Jefferson County						June 22, 2026

# Fayette, MS							Permit Writer: Rajeev Gupta

# Water II Branch

# FACILITY INFORMATION

## Nature of Business: Municipal Solid Waste Landfill.

## Process Wastewater Description: Leachate generated from waste disposal activities

## Proposed Flowrate: 0.072 MGD (Currently the facility is permitted for 0.024 MGD)

- Applicable Federal Guidelines: 40 CFR Part 445 – Landfills Point Source Category requires compliance with 40 CFR Part 403 – General Pretreatment Regulations for Existing and New Sources of Pollution

# RECEIVING POTW INFORMATION

## POTW Name, Agency Interest No., and Permit No.: Natchez POTW, AI# 13293; MS0024252

## POTW Treatment Type: Biological treatment by means of an activated sludge treatment process followed by disinfection using chlorination.

- POTW Design Flowrate: 5.0 MGD

- POTW Receiving Stream: Mississippi River

- POTW Receiving Stream 7Q10 (Q7/10): 135,000 cfs = 87284 MGD

# PERTINENT FLOWRATE AND LOADING DATA

- POTW 12-month Average Flowrate (QPOTW): 2.10 MGD (December 2024 –November 2025)

- Industrial Facilities Maximum 30-day Average Flow (QIND) in MGD for Contributing Pollutants Data (January 2024 – December 2024):

| Facility (Permit No., AI No.) | Cr | Hg | Cu | Pb | Ni | Ar | Zn | Al | Fe | Se |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Greenway Environmental Services LLC. (MSP092246, 10186) | 0.0208051 | 0.020805 | 0.020805 | 0.020805 | 0.020805 | 0.020805 | 0.020805 | 0.020805 | 0.020805 | 0.020805 |
| Total, QIND (MGD) | 0.020805 | 0.020805 | 0.020805 | 0.020805 | 0.020805 | 0.020805 | 0.020805 | 0.020805 | 0.020805 | 0.020805 |

1Greenway Environmental is only required report annual average and annual maximum flows.  The annual maximum flow for calendar year 2024 was used for conservatism.

- Industrial Facilities Permitted/Requested Flow in MGD (QW):

| Facility (Permit No., AI No.) | Cr | Hg | Cu | Pb | Ni | Ar | Zn | Al | Fe | Se |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Greenway Environmental Services LLC. (MSP092246, 10186) | 0.072 | 0.072 | 0.072 | 0.072 | 0.072 | 0.072 | 0.072 | 0.072 | 0.072 | 0.072 |
| Total, QT (MGD) | 0.072 | 0.072 | 0.072 | 0.072 | 0.072 | 0.072 | 0.072 | 0.072 | 0.072 | 0.072 |

2The requested annual maximum flow limit was used as a conservative measure.

.

# BACKGROUND/DOMESTIC LOADING CALCULATIONS

Background Loading (BGL), lb/d = 8.34 x BGC(mg/L) x (QPOTW - QIND )(MGD)

BGC = Background concentration of domestic sewage.

Was not performed due to the large assimilative capacity of the receiving stream.

# ALLOWABLE HEADWORKS LOADING CALCULATIONS

Instream Wastewater Concentration (IWC), % = [QPOTW / (QPOTW + Q7/10)] x 100

IWC % = [2.1/(2.1 + 87284)]*100 = 0.0024 %

Only Acute screening is performed because the IWC < 1%.

Due to the very low IWC for the discharge from the POTW into the Mississippi River, any limits for the landfill would be based on POTW inhibition levels and technical judgement.

- AHL, POTW Inhibition Based (AHLINH)

## AHLINH, lb/day = 8.34 x QPOTW (MGD) x CINH (mg/L)

CINH = Activated Sludge Inhibition Levels, from EPA Guidance Manual on the Development

and Implementation of Local Discharge Limitations Under the Pretreatment Program: Appendix G- Literature Inhibition Levels.  For all parameters except Silver and Arsenic, 1.0 mg/L is used since this value is near the minimum side of the minimum reported range of

inhibition threshold levels.  Inhibition threshold levels could not be found for Iron,

Aluminum and Selenium.

AHLINH (Cr) = 8.34*2.1*1.0 = 		17.5 lb/day

AHLINH (Hg) = 8.34*2.1*1.0 = 		17.5 lb/day

AHLINH (Cu) = 8.34*2.1*1.0 = 		17.5 lb/day

AHLINH (Pb) = 8.34*2.1*1.0 = 		17.5 lb/day

AHLINH (Ni) = 8.34*2.1*1.0 = 		17.5 lb/day

AHLINH (As) = 8.34*2.1*0.1 = 		1.75 lb/day

AHLINH (Zn) = 8.34*2.1*1.0 = 		17.5 lb/day

Inhibition should not be an issue based on the permitted flow rates and the concentrations of the pollutants of concern reported in the application for Waste Management and Greenway Environmental Services LLC.

- AHL, POTW NPDES Permit Limit Based (AHLNPDES)

If POTW has a limit for a specific parameter, industrial loading is limited to the amount the POTW can accept and still meet the limit.  The POTW’s NPDES Permit does not contain any limits for the pollutants of concern.

- PROPOSED PERMIT LIMITATIONS

| Parameter | Allowable Concentration (ALL) |  | Categorical Limits (CAT) |  | Current Permit Limits (CPL) |  | Proposed Permit Limits (PPL) |  | Basis |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Avg. (mg/L) | Max. (mg/L) | Avg. (mg/L) | Max. (mg/L) | Avg. (mg/L) | Max. (mg/L) | Avg. (mg/L) | Max. (mg/L) |  |
| Ammonia (as N) | ----- | ----- | ----- | ----- | Report | Report | Report | Report | CPL |
| COD | ----- | ----- | ----- | ----- | Report | Report | Report | Report | CPL |
| Nitrite +Nitrate Nitrogen | ----- | ----- | ----- | ----- | Report | Report | Report | Report | CPL |
| Total Nitrogen | ----- | ----- | ----- | ----- | Report | Report | Report | Report | CPL |
| Chromium, TR | ----- | ----- | ----- | ----- | Report | Report | Report | Report | CPL |
| BOD5 | ----- | ----- | ----- | ----- | Report | Report | Report | Report | CPL |
| Arsenic, TR | ----- | ----- | ----- | ----- | Report | Report | Report | Report | CPL |
| Copper, TR | ----- | ----- | ----- | ----- | Report | Report | Report | Report | CPL |
| Lead, TR | ----- | ----- | ----- | ----- | Report | Report | Report | Report | CPL |
| Nickel, TR | ----- | ----- | ----- | ----- | Report | Report | Report | Report | CPL |
| Zinc, TR | ----- | ----- | ----- | ----- | Report | Report | Report | Report | CPL |
| Aluminum, TR | ----- | ----- | ----- | ----- | ----- | ----- | Report | Report | TJ |
| Iron, TR | ----- | ----- | ----- | ----- | ----- | ----- | Report | Report | TJ |
| Selenium, TR | ----- | ----- | ----- | ----- | ----- | ----- | Report | Report | TJ |
| Flow | ----- | ----- | ----- | ----- | Report | 0.024 MGD | Report | 0.072 MGD | POTW |
| pH | ----- | ----- | ----- | ----- | ----- | ----- | 6.0 S.U. (min) | 9.0 S.U. | TJ |

TR = Total Recoverable; T = Total

PPL is the smallest of ALL, CAT, and CPL, average and maximum, respectively

TJ = Technical Judgement

As is found in the existing permit, monitoring only is being required for all Toxics.  Monitoring for Total Recoverable Aluminum, Total Recoverable Iron and Total Recoverable Selenium is being added to the permit based on Technical Judgement.  Total Recoverable Mercury monitoring is not being required based on the small concentration reported in the effluent in the application.  All pollutants shall be monitored quarterly with a grab sample of the effluent.  This is being changed from semiannually because of the increased flow to the POTW.  Flow shall be measured once per batch using batch measurement.  pH shall be monitored weekly with a grab sample of the effluent.  A letter has been received from the City of Natchez indicating that they are willing to accept the increased discharge.  pH limits are based on Technical Judgement.

NATCHEZ POTW REMOVAL EFFICIENCIES

| [mg/L] | 09/08/21 | 09/22/21 | 10/13/21 | 10/26/21 | 11/10/21 | 11/30/21 | 12/07/21 | 12/21/21 | 01/12/22 | 1/26/22 | 2/8/22 | 2/16/22 | Removal Efficiency1 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Cd Inf. | 0.00005 | 0.00005 | 0.00005 | 0.00005 | 0.00005 | 0.0001 | 0.0001 | 0.0001 | 0.00005 | 0.00005 | 0.0001 | 0.00005 | 50% |
| Cd Eff. | 0.00005 | 0.00005 | 0.00005 | 0.00005 | 0.00005 | 0.00005 | 0.00005 | 0.00005 | 0.00005 | 0.00005 | 0.00005 | 0.00005 |  |
| Cr Inf. | 0.002 | 0.001 | 0.001 | 0.002 | 0.001 | 0.002 | 0.005 | 0.019 | 0.003 | 0.001 | 0.002 | 0.001 | 65 % |
| Cr Eff. | 0.0005 | 0.0005 | 0.0005 | 0.0005 | 0.0005 | 0.0005 | 0.001 | 0.005 | 0.002 | 0.001 | 0.001 | 0.001 |  |
| Cu Inf. | 0.0242 | 0.0267 | 0.0374 | 0.0367 | 0.0285 | 0.0265 | 0.0503 | 0.0519 | 0.0216 | 0.0169 | 0.0235 | 0.0234 | 68.8 % |
| Cu Eff. | 0.0096 | 0.0093 | 0.0097 | 0.0116 | 0.0086 | 0.0129 | 0.0113 | 0.0071 | 0.0093 | 0.0062 | 0.0085 | 0.0106 |  |
| Pb Inf. | 0.002 | 0.0034 | 0.0031 | 0.0028 | 0.0030 | 0.0033 | 0.0101 | 0.0062 | 0.0021 | 0.0019 | 0.003 | 0.0029 | 78.6% |
| Pb Eff. | 0.00025 | 0.0005 | 0.0006 | 0.0008 | 0.0006 | 0.0008 | 0.0015 | 0.001 | 0.0006 | 0.0008 | 0.0008 | 0.0011 |  |
| Ni Inf. | 0.003 | 0.0032 | 0.003 | 0.0031 | 0.0021 | 0.0035 | 0.0072 | 0.0046 | 0.0028 | 0.0025 | 0.0034 | 0.0023 | 46.7 % |
| Ni Eff. | 0.0016 | 0.0022 | 0.0024 | 0.0014 | 0.0011 | 0.0018 | 0.0022 | 0.0022 | 0.0023 | 0.0014 | 0.0015 | 0.0016 |  |
| Ag Inf. | 0.00005 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0003 | 0.00005 | 0.00005 | 0.00005 | 0.0001 | 0.0001 | 60% |
| Ag Eff. | 0.00005 | 0.00005 | 0.00005 | 0.00005 | 0.00005 | 0.00005 | 0.00005 | 0.00005 | 0.00005 | 0.00005 | 0.00005 | 0.00005 |  |
| Zn Inf. | 0.103 | 0.077 | 0.080 | 0.085 | 0.077 | 0.077 | 0.157 | 0.147 | 0.075 | 0.059 | 0.088 | 0.081 | 63% |
| Zn Eff. | 0.029 | 0.034 | 0.037 | 0.039 | 0.031 | 0.041 | 0.039 | 0.031 | 0.035 | 0.023 | 0.036 | 0.034 |  |
| CN Inf. | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 62 %* |
| CN Eff. | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 |  |
| As Inf. | 0.0012 | 0.0021 | 0.0014 | 0.001 | 0.0007 | 0.0011 | 0.003 | 0.0025 | 0.0011 | 0.0010 | 0.0008 | 0.0006 | 38.2% |
| As. Eff. | 0.0008 | 0.0011 | 0.0006 | 0.001 | 0.00025 | 0.00025 | 0.0017 | 0.0011 | 0.0008 | 0.0009 | 0.0011 | 0.0006 |  |

1 Removal Efficiency = [(<inf.> - <eff.>)/<inf.>]*100, where <inf.> is the average influent value and <eff.> is the average effluent value.

Grey-shaded values were excluded in calculating removal efficiencies because the influent < effluent for the same sample date.

Blue values were used in “non-detect” results obtained from the POTW bench sheets in which the MQL (Method Quantitation Limit) was then divided by 2 to obtain the blue value.

*MDEQ-observed study removal efficiency for activated sludge systems was used due to inadequate data from the POTW.

ADEQUACY OF TREATMENT

Date: June 22, 2026

Permit Writer: Rajeev Gupta

Site: Greenway Environmental Services LLC., Green Meadow Sustainable Solutions Landfill

Pretreatment Permit No. MSP092246

Jefferson County

Proposed Hydraulic Loading:  0.050 MGD 	Proposed Increase in Flowrate: 0.072 mgd

Proposed Organic Loading: 1520 mg/L (Maximum value provided on DMR’s for 2023 calendar year)

0.072 MGD*8.34*1520 mg/L = 912.7 lb/day

Natchez POTW, NPDES Permit No. MS0024252, AI No. 13293

Permitted Flow:	5.0 MGD (Monthly Average Limit)

12 Months Flow:	2.1 Monthly avg. value (from December 2024–November 2025DMRs)

12 Months BOD5: 300 mg/L representative influent value

Design BOD5: 5 MGD*8.34*300 mg/L = 12510 lb/day

Average BOD5: 2.1 MGD*8.34*300 mg/L = 5254 lb/day

Evaluation of Flow

5 MGD permitted – 2.1 MGD actual = 2.9 MGD

2.9 MGD available vs. 0.072 MGD proposed increase in flowrate

Evaluation of BOD5

12510 lb/day Design– 5254 lb/day Average = 7256 lb/day

7256 lb/day available vs. 912.7 lb/day proposed